## CAS v2.0
No | Date | Question/Issue | Change or response | Fixed in version

## CAS v1.1.3
No | Date | Question/Issue | Change or response | Fixed in version
1 | 2014-06-23 | issues in test configurations: SmallGrid, MiniGrid, MicroGrid were reported | New versions of the test configurations are issued. Changes are not described in detail. Error test configuration is now available
2 | 2014-06-17 | Conformity Assessment Scheme Document List Please correct the description of “2.2. CGMES v2.4.14”: it’s the same description about “2.1. CGMES Conformity Assessment Framework v1.0.0” | The text is changed to refer to CGMES v2.4.14
3 | 2014-06-17 | Operational Procedure: Please specify if after First Party Assessment process the declaration of conformity issued by a Vendor will be publicly available into ENTSOE website also if the vendor don’t want to continue the process further to Second Party Assessment. | It is already speified in the figure 1 "Communication martix". The Declaration of Conformity will be on the ENTSO-E web site
4 | 2014-06-17 | Test Procedures and Conformity Categories: • The Vendor is obliged to use validation tools for exported instance files ? CimSpy will be fine ? • The Vendor is obliged to use internal validation tools for imported instance files ? • Please specify what is intended for ‘internal validation’ performed by the Application and the required levels of Errors reporting • Error/Unstructured Test Cases (not published in advance) will be performed for every Test Use Case ? • Conformity Tests should be performed on all the available Test Configurations ? For example, ‘TUC 2 – import of Equipment’: should be also import EQ instance file of Test Configuration with HVDC even if the Application doesn’t handle CGMES-HVDC modeling ? | - Yes, it is specified in section 2.1 "During the First party assessment the Supplier shall use available validation tools to validate the instance data during different test steps". Text has been added to specify that ENTSO-E has no requirement which tool should be used. - yes, suppliers should be able to check the what they are importing and report errors/warnings to the users. This is a basic feature to ensure that importes as well as the exports performed by the application are correct. No change was applied to the documentation. - CGMES [R.4.3.4.4] defines some errors that needs to be reported by the tools. In addition all deviations from CGMES should be reported, i.e. the application should be able to report to the user where the the problem is in the instance files that are imported. Also covered in the previous answer. No change was applied to the documentation. - as described in section 2.5 the reviewers will give guidance on this. It will not be for every TUC. Selective approach will be applied. - yes the conformity tests shall be performed with all available test configurations. This is specified in section 3.5 "An Application, subject to conformity assessment, shall get score “Pass” to a given TUC only if the Application gets score “Pass” using all test configurations applicable to this TUC...." On the specific example the focus on the HVDC is handled in TUC41. There are also CGMES requirements [R.4.1.6], [R.4.1.7], [R.4.1.8] on the import/export of optional and mandatory attributes.
5 | 2014-06-17 | Test Use Cases: • TUC 1: import only TP and EQ Boundary: is mandatory ? shouldn’t it be ‘not required’ for load-flow Applications ? as TUC 2-8 ? • TUC 9-11: is required the import of only 1 MAS or also MAS + BOUNDARY ? • Please specify how perform TUC from 1 to 8: should the tool import only the required instance file from a zip package or it could import the entire package with other profiles data? • Please specify how perform TUC from 13 to 20: should the tool export only the required instance file from a zip package or it could export the entire package with other profiles data ? • TUC 25-26-27: in this Use Cases import and export of difference files are both needed and the required level for load-flow analysis tools is ‘Bronze’. Instead, TUC 10-11-22-23 related to Import/export of difference instance date for one/more profiles are marked with ‘Silver’ or ‘Gold’. Why these different grades ? • TUC 40 “Maintain hierarchy of the model”: please explain more deeply this Use Case and add CGMES references | - There is no load flow involved in the process in TUC 1. Same for othet TUC related to the import. Please see the 140623_CGMES_ConformityAssessment_TestDefinitions_and_TestReportTemplate_v1.0.1.xlsx where the test steps are defined. - in TUC 9 you need to be able to have solved or unsolved MAS. For most of the test configurations you need to import boundary in order to comoplete the dangling references. This TUC is related to the ability to import multiple profiles. - you should demontsrate import only of the menetioned instance file. these TUC are designed for sustems that support only specific profiles. For toold performing load flow etc. please refer to the text in Chapter 3.3 and Chapter 4 in the 140623_CGMES_ConformityAssessment_TestProceduresConformityCategories_v1.0.1.docx as well as in the 140610_CGMES_ConformityAssessment_FunctionCategoryMatrix_v1.0.0.xlsx - Different grades are assigned for TUC for different functions because e.g. it is considered that an application that can do load flow it is very basis to be able to manage boundary set. this is why it is set to Bronze. -the text of TUC 40 was edited.
6 | 2014-06-20 | Data Management -> Import : TUC 1 to TUC 9 belong to this category for Bronze level assessment. If the application is not supporting the BD, TN and DL import, can it still opt for Bronze level assessment with rest of the TUC’s ? | Yes, please refer to the Note which is below the table – FunctionCategoryMartix.xls. No change in the documentation
7 | 2014-06-20 | TUC 03 belongs to import of Topology profile, which means it should be used with Bus-Branch network models. Is that a correct assumption? | Available test configurations which are node breaker type also have TP instance file.. Therefore you should test these as well. No change in the documentation
8 | 2014-06-20 | TUC 40 “Maintain hierarchy of the model” : Could you provide more details on what kind of hierarchy maintenance is expected within the application for this test? | For instance you should have Substation, VoltageLevel, etc. and maintain this in your application. The text of TUC 40 was edited.
9 | 2014-06-20 | Similar to #1 above, if an application is not supporting difference files, profile exports but is able to import assembled models of Type1 / Type 2 / Base Case and run Short Circuit analysis, then is it still allowed to opt for remaining tests for Bronze level assessment in that functional category? | From what you are describing, it should fit to what is required to get at least Bronze for Short Circuit function. No change in the documentation
10 | 2015-05-29 | MicroGrid Test Configuration In cases where the transformer tap control is enabled (load flow with transformer regulation): The “TapChangerControl" (ID: 5fc492ab-fe33-423b-84f1-a47f87552427) is defined at terminal “BE-TR2_1 - T2” (ID: 2cd21c77-b8b1-4896-95fb-240f45b9ac89). The results for this terminal show a negative active power (- 64.502 MW (load oriented)), however the transformer “TapChangerControl” has a positive active power target set point (+65 MW). According to CIM Profile: “For flow control load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment.” This seems to be a problem in the conformity test example: a) the sign of the active power target set point should be rotated (set to -65MW); or b) the selected terminal for the “TapChangerControl” should be on the opposite side of the transformer. | The issue is fixed applying option a). Set-point is target is changed to -65 (changed the sign). The changes are in each BE SSH files (in all configurations, including the BE SSH files in difference folders) | 1.1.2
11 | 2015-05-29 | The name parameter “IdentifiedObject.name” is missing for all “DiagramObject”. According to the profile (UML), the “DiagramObject” is derived from the “Core::IdentifiedObject”, so the “IdentifiedObject.name” should be defined. We received the following comment (28 October, 2014): “We never exported name for diagram object and never god this issue reported. More important CimDesk also does not report this as an issue. Adding it (althought there is no reason to have name for diagram object except to increase size of a file) would require would requiere all models to be redone which would require time, so we leave it as is at the moment”. This issue has already been stated in the MicroGrid Test Documentation, but should be resolved to avoid having exceptions in the conversion rules which apply to test cases only. | all variants of the MicroGrid test configuration are fixed - IdentifiedObject.name for DiagramObject is added. The note in the documentation file is also deleted. all variants of the MiniGrid test configuration are fixed - IdentifiedObject.name for DiagramObject is added. The issue was mainly for the node-breaker versions The names added for the TextDiagramObject in the SmallGrid Test configurations. IdentifiedObject.name for DiagramObject is also added for SmallGrid Test configurations | 1.1.2
12 | 2015-05-29 | MicroGrid_BC_Assembled (with area control) “BE” contains a “ControlArea” defined with the following option: “ControlArea.type = AGC” (= used for automatic generation control). The two generators (“GeneratingUnit”) involved are set as follows: GeneratingUnit: “Gen-1229753060” (ID: 18993b11-2966-4bce-bab9-d86103f83b53) associated with generator “BE-G1” (ID: 3a3b27be-b18b-4385-b557-6735d733baf0) “GeneratingUnit.genControlSource” = offAGC GeneratingUnit: “Gen-1229753024” (ID: 5b7a4d43-09ec-4033-882d-64a76d557631) associated with generator “BE-G2” (ID: 550ebe0d-f2b2-48c1-991f-cebea43a21aa) “GeneratingUnit.genControlSource” = offAGC We assume that this parameter in the “GeneratingUnit” should be set to “onAGC” when the generator is involved with the area control, and not to “offAGC”. Unfortunately there is no detailed information available in the corresponding CIM Profile. | fixed as suggested | 1.1.2
13 | 2015-05-29 | MicroGrid_T1_Assembled Issue already reported via email on 27 October, 2014: The test case contains an “EnergySource” model with the following data: voltageAngle = -0.113848 rad => -6.523 deg voltageMagnitude = 21.987 kV => 1.047 p.u. based on 21 kV r = 0.007662 Ohm x = 0.076618 Ohm According to the CIM ENTSOE 2.4.14/15 profile, the “voltageAngle” and “voltageMagnitude” attributes are defined as follows: “voltageAngle” = Phase-to-phase open circuit voltage magnitude; and “voltageMagnitude” = Phase-to-phase open circuit voltage magnitude. Therefore, the “EnergySource” model is a voltage source behind an impedance and the “voltageAngle” and “voltageMagnitude” parameters define the internal voltage set point (open circuit voltage) of the source. However, the results show that the voltage source uses the “voltageAngle” and “voltageMagnitude” parameters to control the voltage at the corresponding connected busbar ( -> closed circuit voltage). We received the following comment (28 October, 2014): At the moment we can do nothing about it, any change would require changing XXXX model and testing. We would also propose to change meaning of those two parameters to the way we are using them since we find it much more logical and useful. Current description of internal voltage of energy source and open circuit angle (phase angle of the the independent device while it is disconnected from the network???). Connecting such device to the network would result in results difficult to predict. On a mid/high voltage all devices are controlling voltage and angle on busburs so we think we should follow this here. This is not in line with the CIM ENTSO/E profile, which states that the “voltageMagnitude” and “voltageAngle” parameters should be interpreted as an “open circuit” voltage and not as a “closed circuit” voltage. We suggest the following: a) the test case (results) must be adapted; b) the CIM profile should be changed; or c) this test case should be removed from the conformity test. | No change applied. An issue is recorded in the CGMES issue ist. The reviewers should consider this in the review process.
14 | 2015-05-29 | MicroGrid_T2_Assembled In cases where the transformer tap control is enabled (load flow with transformer regulation): Transformer “NL_TR2_HVDC1” is a “TapChangerControl” model (ID: da7fa470-044a-42e6-afb7-c6c01e028a07) defined with the following data: targetDeadband = 0.5 kV targetValue = 123.9 kV So the regulating range of the transformer tap is: Ureg(min) = 123.9 kV – 0.5kV/2. = 123.65 kV (or 99.798 %) Ureg(max) = 123.9 kV + 0.5kV/2. = 124.15 kV (or 100.2 %) The load flow results, however, show a voltage higher than 124.15kV (100.2 %); see “NL_Busbar_HVDC1” = 105.50%. The controlled voltage is outside the regulating control range. We assume that the “targetDeadband” of this “RegulatingControl” is not correctly set and should be changed (+/- 0.5 kV is too narrow). | Its seems that there is no problem here. Probably looking at the wrong results (without trafo control). "Figure 8 Type 2 – assembled" shows that the voltage is 100.35% and not 105.5% as reported
15 | 2015-05-29 | MicroGrid_T3_Assembled All “CsConverter” are configured as lossless (“idleLoss” = 0, “resistiveLoss” = 0 and “switchLoss” = 0). However, the load flow results show that the converters do in fact have losses (75 MW <-> 74.688 MW). We assume that this is an error in the conformity test example. The “switchLoss” parameter should not be zero. To achieve the same results in PowerFactory, the “Switch Loss Factor” should be set to 0.0012267 MW/A (in the CIM model) or 1.2267 kW/A (in the PowerFactory model) for all rectifier/inverter models. | Results are updated, so there are no losses on the converters (DOC and XLS documents updated). | 1.1.2
16 | 2015-05-29 | We detected an issue involving all test cases with a boundary model and corresponding “EquivalentInjection” objects: According to the CIM CMGES equipment profile, “[a] “ConductingEquipment” must have either a “BaseVoltage” association or be within a “VoltageLevel” ” (see OCL constraints for “ConductingEquipment”). This constraint is not fulfilled in the MiniGrid and MicroGrid test cases for “EquivalentInjection” instances which are connected to the boundary. As the current ENTSO-E boundary definition has no “VoltageLevel” instances, the “EquivalentInjections” are therefore required to have a “BaseVoltage” association. Strict application of the profile and its constraints would force vendor applications to not accept the previously mentioned test cases, or to ignore the equivalents upon import. | This is fixed for all MiniGrid, SmallGrid and MicroGrid test configurations. BaseVoltage is agged to all EquivalentInjections | 1.1.2
17 | 2015-05-31 | RealGrid Test configuration does not comply with CGMES rule [R.4.1.2.3]. The OperationalLimitType rdf:ID doesn't start with '_' | Fixed. "_" is added to the rdf:ID | 1.1.2
18 | 2015-05-31 | MiniGrid_BC_Complete (common) For the “SynchronousMachine”, the values of “SynchronousMachine r2” are equal to “SynchronousMachine.r” for the three Generators (G1 – G3). This also applies to “SynchronousMachine.x2” and “SynchronousMachine.satDirectSubtransX”. According to the CIM ENTSOE 2.4.15 profile, the positive sequence resistance is defined in “Ohm” (Type: Resistance) and the zero- and negative sequence resistances in “p.u.” (Type: PU). To obtain correct results using the modelled IEC 60909-4 example, Z1 = Z2 must be used, which cannot be done due to the abovementioned difference in units. From our point of view, if the negative sequence impedance should equal the positive sequence impedance, the parameter “SynchronousMachine.r2” should be set as follows: Generator G1, ID SynchronousMachine.r = 0.002 Ohm SynchronousMachine.r2 = 0.00068 p.u. (was set to 0.002 p.u.) Generator G2, ID: 2970a2b7-b840-4e9c-b405-0cb854cd2318 SynchronousMachine.r = 0.05 Ohm SynchronousMachine.r2 = 0.004535 p.u. (was set to 0.05 p.u.) Generator G3, ID: 392ea173-4f8e-48fa-b2a3-5c3721e93196 SynchronousMachine.r = 0.018 Ohm SynchronousMachine.r2 = 0.00163 p.u. (was set to 0.018 p.u.) | All Mini Grid bus branch and node breaker test configurations(MiniGrid Base Case, MiniGrid Type1 and MiniGrid Type2) have been changed. List of changes: EQ files- SynchronousMachines: 1) SynchronousMachine ID: _2970a2b7-b840-4e9c-b405-0cb854cd2318 changed line: from: <cim:SynchronousMachine.r2>0.005</cim:SynchronousMachine.r2> to: <cim:SynchronousMachine.r2>0.004535</cim:SynchronousMachine.r2> 2) SynchronousMachine ID: _ca67be42-750e-4ebf-bfaa-24d446e59a22 changed line: from: <cim:SynchronousMachine.r2>0.002</cim:SynchronousMachine.r2> to: <cim:SynchronousMachine.r2>0.00068</cim:SynchronousMachine.r2> 3) SynchronousMachine ID: _392ea173-4f8e-48fa-b2a3-5c3721e93196 changed line: from: <cim:SynchronousMachine.r2>0.018</cim:SynchronousMachine.r2> to: <cim:SynchronousMachine.r2>0.00163</cim:SynchronousMachine.r2> | 1.1.2
19 | 2015-05-31 | MiniGrid_BC_Complete (phase-to-ground short-circuit) The test results for phase-to-ground short-circuits are still not conformant with the official IEC 60909-4 test results. See Table 13, Chapter 6.3.2 (IEC 60909-4): Fault Ik1 (IEC 60909) Ik1 (CGMES Test case) ip (012) (IEC 60909) ip (012) (CGMES Test case) Bus 2 15,9722 kA 15,979 kA 39,9641 kA 39,331 kA Bus 3 10,4106 kA 10,3951 kA 24,2635 kA 24,0663 kA Bus 4 9,0498 kA 9,04132 kA 21,0415 kA 20,8661 kA Bus 5 17,0452 kA 17,0301 kA 41,4303 kA 41,0667 kA Chapter 6.1 of the IEC 60909-4 contains the following statement: “The result given in table 12 and 13 should be reached, to declare a good correspondence between the calculated results and the given results. This is necessary… . If there are deviations, they should be smaller than +- 0.02 %.” However, the differences are greater than this (e.g. for “Bus 5” fault, and the “ip” results). One possible reason for the discrepancy in results is incorrect zero sequence impedances of the three-winding transformers “T4” and “T5”, when compared to the impedance provided in the IEC standard. | No changes related to this issue. Transformers T3 and T4 are in parallel and they have identical parameters. Zero impedance of T4 is taken from IEC Standard 60909-04, chapter 2.2. | 1.1.2
20 | 2015-05-31 | SmallGrid Test configuration boundary set is missing - short names and descriptions for Line, Junction and ConnectivityNode - the terminal has the associaion Terminal.ConnectivityNode which is nt defined in the profile | fixed. Short names and description added. The association of the terminal with connectivity node are deleted | 1.1.2
21 | 2015-05-31 | Terminal sequence number missing for the EquivalentBranch for Small Grid bus branch test configuration | fixed. The sequence numbers added to the terminals of the EquivalentBranch in the model | 1.1.2
22 | 2015-05-31 | The validation reports for the MicroGrid Test configuration are outdated | the documentation is updated | 1.1.2
23 | 2015-05-31 | There is an issue in Small Grid Models. For some lines (or all of them, eg. _045e3524-c766-11e1-8775-005056c00008), the limits are only defined for one end. In CIM it is stated: "The PATL limits must be specified for all Transformers and at both ends of the ACLineSegment". "At least one of the limit types must be provided (this is the minimum requirement)" In small grid we have limits only assigned to the terminal with sequence number 1. | to be analysed and fixed in the next version of the test configuration
24 | 2015-05-31 | Wrong dependencies in the headers of Mini Grid and Small Grid Test configurations | The dependencies in the file headers of MiniGrid and SmallGrid test Configurations are fixed | 1.1.2
25 | 2015-05-31 | MiniGrid test configuration In the CGMES_v2.4.15_MicroGridTestConfiguration_T4_Assembled_BB_Complete_v2 there is a SeriesCompensator (rdf:ID = _df16b3dd-c905-4a6f-84ee-f067be86f5da), that is not part of ACLineSegment. One end of this Series compensator end in the TopologicalNodе (rdf:ID = _23b65c6b-2351-4673-89e9-1895c7291543) that has no any other things connected. | There is a indeed problem in model. It is not a problem of export, or some CIM related problem, its just that the connection is at the wrong nodes (probably this happened when breakers were added). This was hard to see on the diagram. To be fixed in the next version of the test configuration
26 | 2015-05-31 | An issue reported on the very old file MiniGridTestConfiguration_BC_EQ_v7.0.0.xml For PowerTransformer _813365c3-5be7-4ef0-a0a7-abd1ae6dc174, all of the R and X values are on the low voltage winding (_0a33f633-7415-4f95-b3c2-f3ddbee92644) instead of the high voltage winding (_4864d0c6-f4ca-477a-b944-9927edb37fa6). This is prohibited by profile 2.4.15 in section 3.9.32 | This needs to be checked in the last versions if the test configuration and fixed in the next release
27 | 2015-05-31 | we have discovered an issue with the Microgrid Type 1 test configuration. In detail, in the file named “MicroGridTestConfiguration_T1_BE_EQ_DIFF2_V2.xml” you can find the declaration of a new Terminal object: <cim:Terminal rdf:ID="_933972e9-dc35-4899-929b-4e217623cde9"> <cim:IdentifiedObject.name>BE-TR2_2</cim:IdentifiedObject.name> <entsoe:IdentifiedObject.shortName>BE-T_2</entsoe:IdentifiedObject.shortName> <cim:ACDCTerminal.sequenceNumber>1</cim:ACDCTerminal.sequenceNumber> <cim:Terminal.phases rdf:resource="http://iec.ch/TC57/2013/CIM-schema-cim16#PhaseCode.N"/> <cim:Terminal.ConductingEquipment rdf:resource="#_1e951716-1c9e-413f-b919-9f822df4b38a"/> <cim:Terminal.ConnectivityNode rdf:resource="#_56ca173b-fd2d-4ef3-bc32-4ae86a318c39"/> </cim:Terminal> In this case, it is also mandatory to specify the topology profile attributes for this Terminal into the file “MicroGridTestConfiguration_T1_BE_TP_DIFF2_V2.xml”. However, such file has not been created yet. | Indeed this TP difference file should be created and include data for this new terminal in it. This will be done in the next update test configurations
28 | 2015-05-31 | ControArea in the model CGMES_v2.4.15_MicroGridTestConfiguration_BC_Assembled_CA_v2. In the model CGMES_v2.4.15_MicroGridTestConfiguration_BC_Assembled_CA_v2 ControlArea is defined in BE MAS. However ControlAreaGeneratingUnitis not defined . The modelling of the ControlArea should be improved according to the profile | to be analysed and fixed in the next version of the test configuration
29 | 2015-06-01 | RealGrid Test configuration update | The main updates are: - Static VAR compensator are exported as StaticVarCompensator (instead of LinearShuntCompensator) - VoltageLevel.highVoltageLimit and VoltageLimit.lowVoltageLimite attributes are exported - For a two terminal PowerTransformer connected to the same voltage level, non zero values r and x are on the high voltage PowerTransformerEnd (correction of the issue below) - TapChangerTablePoint.x attribute is exported in PerCent (instead of Ohm) - Documentation is updated - Load flow spreadsheet is updated | 1.1.2
30 | 2015-06-12 | Issue found in the file header of files edited on 29 and 31 May 2015. the issue is that: - rdf:ID is used in the file header instead of rdf:about - there is # in the ID i.e. rdf:about="#urn:uuid:5f7603dc-eab2-4876-a5fc-366587139c5a"> which is wrong | The issue was filed for all files - rdf:ID is replaced by rdf:about - # is deleted from the rdf:ID string in the header | 1.1.3
31 | 2015-06-12 | There is one TopologocalIsland reported in MicroGridTestConfiguration_BC_NL_SV_V2.xml but none in MicroGridTestConfiguration_BC_BE_SV_V2.xml The TopologocalIsland refer to topological nodes in both • MicroGridTestConfiguration_BC_BE_TP_V2.xml • MicroGridTestConfiguration_BC_NL_TP_V2.xml This can’t be right. I would expect one TopologocalIsland with different IDs per MAS. As data for each MAS is created by independent organizations it is not possible that they can • Create TopologocalIslands including neighboring TopologicalNodes. • Rely on a TopologocalIsland in an SV coming from another MAS | Indeed each MAS should have a TopologicalIsland. The Assembled model will have a different TopologicalIsland which is created at the time the SV is exported. The issue with the test configuration will be checked and fixed in the next update